Good Afternoon

We have received our results from the lead in water retesting. The five water fountains that previously failed, all easily fell below the limit of 15 parts per billion. These outlets will be put back into service immediately. Unfortunately, the sink in the dental office still did not meet the states requirements. We will perform more remediation and have the outlet retested. Until we receive desirable results the sink will have a sign stating that it is not suitable for drinking. Below is a table with updated results.

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Downsville Central School Lead in Water Results** | | | | | | |
| **Water Outlet Location** | **Prior Results** | **Retest Date** | **Results Obtained** | **Lead Amount** | **Lead Limit** | **Units** |
| 2nd Floor Drinking Fountain Left | 0.0200 | 12/14/2016 | 1/12/2017 | < 0.0010 | 0.015 | mg/L |
| 2nd Floor Drinking Fountain Right | 0.0197 | 12/14/2016 | 1/12/2017 | < 0.0010 | 0.015 | mg/L |
| Principal's Office Drinking Fountain Left | 0.0397 | 12/14/2016 | 1/12/2017 | < 0.0010 | 0.015 | mg/L |
| Principal's Office Drinking Fountain Right | 0.0400 | 12/14/2016 | 1/12/2017 | < 0.0010 | 0.015 | mg/L |
| Cafeteria Drinking Fountain | 0.0178 | 12/14/2016 | 1/12/2017 | 0.0047 | 0.015 | mg/L |
| Dental Office Room 125 Sink | 0.0160 | 12/14/2016 | 1/12/2017 | 0.0200 | 0.015 | mg/L |

Thank you for your understanding and patience during this process.