## Summary
| Requirement Forecast Report - Summary |  |  |  | DRAFT
Yellow Springs Schools
Yellow Springs High School/McKinney Middle School
Detailed Assessment with Costs
May 9, 2019 |  |  | Revised: | TBD
[7 empty] | Critical | Priority | Deferred
|  | Subtotal Construction Cost | 13422616.9494 |  | Architectural | 7324565.545 | 2898522.615 | 2507727.85 | 1918315.08
| Design Contingency | 10% | 1342261.6949 |  | HVAC/Plumbing | 3655297.3 | 321916 | 3142207.8 | 191173.5
| Contractor General Conditions | 5% | 671130.8475 |  | Electrical | 1249330 | 222687 | 424567 | 602076
| Project Contingency | 7% | 939583.1865 |  | Technology | 600999.46 | 279841.66 | 261466.2 | 59691.6
| Phasing Costs | 3% | 402678.5085 |  | Site | 592424.6444 | 276485.9444 | 284127.2 | 31811.5
|  | Total Estimate of Probable Construction Costs | 16778271.1868 |  | Subtotal Construction Cost |  | 3999453.2194 | 6620096.05 | 2803067.68
| Project Soft Costs | 18% | 3020088.8136 |  | Design Contingency (10%) |  | 399945.3219 | 662009.605 | 280306.768
[5 empty] | Contractor General Conditions (5%) |  | 199972.661 | 331004.8025 | 140153.384
|  | TOTAL Estimate of Probable Project Costs | 19798360.0004 |  | Project Contingency (7%) |  | 279961.7254 | 463406.7235 | 196214.7376
[5 empty] | Phasing Costs (3%) |  | 119983.5966 | 198602.8815 | 84092.0304
| TOTAL AREA (SF) |  | 74229 |  | Total Est. of Probable Construction Costs |  | 4999316.5243 | 8275120.0625 | 3503834.6
[5 empty] | Project Soft Costs (18%) |  | 899876.9744 | 1489521.6113 | 630690.228
| TOTAL RENOVATION COSTS |  | 19798360.0004 |  | Total Est. of Probable Project Costs |  | 5899193.4987 | 9764641.6738 | 4134524.828
| TOTAL COST PER SF (NEW CONSTRUCTION) |  | 258.56 |  | Check (all phases) |  | 19798360.0004
| TOTAL REPLACEMENT COSTS FOR SAME BUILDING AREA |  | 19192650.24
| RENOVATE TO REPLACE RATIO |  | 103.2%

## Arch
Requirement Forecast Report - Architectural
Ratings to be based on the following scoring system
Client: |  | Yellow Springs School |  |  |  | 1. End of useful life |  |  |  | Prioritization Category
Campus: |  | Yellow Springs HS/MMS |  |  |  | 2. In need of Repair/Replacement |  |  |  | 1. Critial - Life Safety, Code, Technology, Security
Asset: |  | Yellow Springs HS/MMS |  |  |  | 3. Condition is satisfactory |  |  |  | 2. Priority - Infrastructure, Maintenance, Roof, Envelope
Building Area: |  | 74229 | sf |  |  | 4. Recently replaced |  |  |  | 3. Deferred - Finishes, Furnishings, Fixtures
[6 empty] | 5. New work is Recommended |  | Prioritization
Building Envelope (less 1988, see below) |  | Quantity |  | Detail (models, sizing, etc.) | Condition | Unit Cost | Total Cost | Yes | No | Critical | Priority | Deferred
| Roofing | 67315 | sf | Replace overall roof system due to current age and anticipated life remaining life. This includes cap flashings/copings, gutters and downspouts, roof drains, piping, insulation and roof access/safety systems. | 1 | 15.01 | 1010398.15 | X |  |  | 1010398.15
| Windows | 67315 | sf | Provide new dual-glazed insulated windows with integral blinds or roller shades, as well as transoms and sidelights throughout 1963 original building. Replace interior glazing above lockers in corridors. In addition, replace greenhouse in 1963 addition. | 1 | 4.84 | 325804.6 | X |  |  | 325804.6
| Foundation | 67315 | sf | Repair various locations of cracked foundation wall or open joints in 1963 and 1988 buildings, repair leaks at walls of mechanical room. | 2 | 0.063 | 4240.845 | X |  | 4240.845
| Exterior walls | 67315 | sf | Tuckpoint several areas of mortar joint deterioration; clean, seal and caulk overall facility where required. Prep and paint exposed steel lintels. Replace damaged exterior wall panels, provide infill masonry where needed and replace railings to meet code. Repoint stone sills and replace control/expansion joints, and wood soffits. | 2 | 12.93 | 870382.95 | X |  | 870382.95
| Exterior Doors | 18 | ea | Replace exterior doors in 1963 and 1999 buildings. | 1 | 2500 | 45000 | X |  |  | 45000
Building Interior (less 1988, see below)
| Structure: Floors and Roofs - 1963 Original Building | 900 | sf | Address structural concerns (exterior wall separation) at east end of intermediate floors of 1963 building. | 2 | 109 | 98100 | X |  | 98100
| Complete replacement of finishes and casework throughout facility | 67315 | sf | Replace all finishes due to age and condition. | 1 | 19.33 | 1301198.95 |  |  |  |  | 1301198.95
| Toilet partitions | 24 | stall | Replace all toilet partitions due to age and condition. | 1 | 1000 | 24000 |  |  |  |  | 24000
| Toilet accessories | 67315 | sf | Replace all toilet accessories due to age and condition. | 1 | 0.2 | 13463 |  |  |  |  | 13463
| Doors, frames, and hardware (non-ADA) | 136 | ea | Replace doors, frames and hardware due to age, condition and non-compliance with ADA guidelines. | 1 | 1300 | 176800 | X |  | 176800
| Art program kiln replacmenet | 2 | ea | Replace art kilns due to age and condition. | 1 | 2750 | 5500 | X |  | 5500
| Remove demountable partitions, install new GWB partitions | 440 | sf | Replace demountable partitions due to age, condition, acoustical values and non-use. | 1 | 9 | 3960 |  |  |  | 3960
| Additional wall insulation | 23578 | sf | Provide additional wall insulation for improved building envelope performance. | 2 | 6 | 141468 | X |  |  | 141468
| Total kitchen equipment replacement | 1728 | sf | Replace food service equipment due to age and condition. | 1 | 190 | 328320 | X |  |  | 328320
| Kitchen hood and cooler/freezer replacement | 2 | unit | Replace kitchen exhaust hood and cooler/freezer due to age and condition. | 1 | 42909 | 85818 | X |  |  | 85818
| Replace stage equipment | 1 | ls | Replace stage equipment due to age and condition in black box theater room. | 1 | 34880 | 34880 |  |  |  |  | 34880
| Acoustical control | 12833 | sf | Provide acoustical surface treatments in the gymnasium, student dining and media center. | 2 | 3.11 | 39910.63 |  |  |  |  | 39910.63
| New systems due to hazardous material removals | 1 | ls | Replacement of gypsum board, acoustical panels/tile ceilings, and lab tables/countertops due to removal by hazardous material abatement. | 2 | 39184 | 194034 | X |  |  | 194034
| Replace non-code-compliant handrails/guardrails | 6 | level | Provide new guardrail and handrails to comply with the OBC. | 2 | 5000 | 30000 | X |  | 30000
| Interior stairwell closure | 6 | level | Provide fire-rated closure around stair towers. | 2 | 5000 | 30000 | X |  | 30000
| Rework non-compliant stair | 6 | level | Enclose open treads at stairways. | 2 | 10000 | 60000 | X |  | 60000
Building Accessibility (less 1988, see below)
| Address accessibility issues within the building | 67315 | sf | Remove and replace (or provide new) signage, toilet fixtures (for accessiblity only), lift at the stage, automatic door operator at main entry, accessible showers science classroom lab stations and toilet facilities. | 2 | 1.2 | 80778 | X |  | 80778
Hazardous Materials (less 1988, see below)
| Abatement of known and suspected hazardous materials present | 67315 | sf | AHERA three-year reinspection reports dated January 2017 indicate several known, assumed and suspected hazardous materials throughout the facility that should be abated. | 2 | 5.54 | 372925.1 | X |  |  | 372925.1
Furnishings (less 1988, see below)
| Student and Staff Furnishings | 67315 | sf | The loose furnishings in this facility overall rate at a 3 or below on a scale of 10 (excellent) to 1 (poor) and therefore should be replaced. | 1 | 7.5 | 504862.5 |  |  |  |  | 504862.5
Building General
| Replacement of 1988 Building Area | 6914 | sf | The 1988 building is comprised of temporary modular classrooms, sourrounded by masonry veneer. The original intent of these type classrooms is for temporary facilities, not extended service over decades. At this point, these facilities have served 31 years, well over their useful life and should be replaced with facilities comparable to a permanent educational facility structure. | 1 | 223.13 | 1542720.82 | X |  | 1542720.82
[6 empty] | Subtotal Project Cost | 7324565.545 |  |  | 2898522.615 | 2507727.85 | 1918315.08
[5 empty] | Estimate Contingency | 10% | 732456.5545 |  |  | 289852.2615 | 250772.785 | 191831.508
[5 empty] | Contractor General Conditions | 5% | 366228.2773 |  |  | 144926.1308 | 125386.3925 | 95915.754
[5 empty] | Project Contingency | 7% | 512719.5882 |  |  | 202896.5831 | 175540.9495 | 134282.0556
[5 empty] | Phasing Costs | 3% | 219736.9664 |  |  | 86955.6785 | 75231.8355 | 57549.4524
[6 empty] | Estimate of Probable Construction Costs | 9155706.9313 |  |  | 3623153.2688 | 3134659.8125 | 2397893.85
[5 empty] | Project Soft Costs | 18% | 1648027.2476 |  |  | 652167.5884 | 564238.7663 | 431620.893
[6 empty] | TOTAL Project Estimate of Probable Costs | 10803734.1789 |  |  | 4275320.8571 | 3698898.5788 | 2829514.743

## HVAC
Requirement Forecast Report - Plumbing/HVAC
Ratings to be based on the following scoring system
Client: |  | Yellow Springs School |  |  |  | 1. End of useful life |  |  |  | Prioritization Category
Campus: |  | Yellow Springs HS/MMS |  |  |  | 2. In need of Repair/Replacement |  |  |  | 1. Critial - Life Safety, Code, Technology, Security
Asset: |  | Yellow Springs HS/MMS |  |  |  | 3. Condition is satisfactory |  |  |  | 2. Priority - Infrastructure, Maintenance, Roof, Envelope
Building Area: |  | 74229 | sf |  |  | 4. Recently replaced |  |  |  | 3. Deferred - Finishes, Furnishings, Fixtures
[6 empty] | 5. New work is recommended |  | Prioritization
|  | Quantity |  | Detail (models, sizing, etc.) | Condition | Unit Cost | Total Cost | Yes | No | Critical | Priority | Deferred
Fire Protection
| Sprinkler | 74229 | sf | No sprinkler system currently exists. Consider adding sprinkler system throughout entire building. | 5 | 4 | 296916 |  | X | 296916
Plumbing
| Sanitary Piping - 1963, 1988, 1999 | 59096 | sf | Original sanitary piping is in fair to poor condition and has exceeded it's useful life. Replace all original sanitary piping. | 1 | 3.5 | 206836 | X |  |  | 206836
| Sanitary Piping - 2002 Addition | 15133 | sf | Existing sanitary piping in the 2002 addition is in good condition. | 3 | 0 | 0 |  | X |  |  | 0
| Domestic Water Piping - 1963, 1988, 1999 | 59096 | sf | Original domestic water piping is a mix of copper and galvanized and should be replaced with copper piping as it has exceeded its useful life. | 1 | 3.5 | 206836 | X |  |  | 206836
| Domestic Water Piping - 2002 Addition | 15133 | sf | Existing domestic water piping in the 2002 addition is in good condition. | 3 | 0 | 0 |  | X |  |  | 0
| Domestic Water Heater - 1963, 1999, 2002 | 1 | ls | 75.1 MBH/98 Gallon Storage - 2018 with separate original 250 gallon storage tank. The storage tank needs to be replaced. | 2 | 15000 | 15000 | X |  |  | 15000
| Domestic Water Heater - 1988 | 1 | ls | 40 Gallon Electric water heater should be replaced due to age. | 1 | 5000 | 5000 | X |  |  | 5000
| Incoming Water Service | 74229 | ls | Existing water service is adequate for current usage. If the existing High School/Junior High is sprinklered, a new water service will be required. | 5 | 25000 | 25000 |  | X | 25000
| Plumbing Fixtures - 1963, 1988, 1999 | 82 | ea | 24 Water Closets, 7 Urinals, 4 Drinking Water Coolers, 21 Sinks, 3 Custodial Sinks, 2 Eyewash/Shower, 17 Showers, 4 Exterior Wall Hydrants need replaced/added. | 1 | 1500 | 123000 | X |  |  | 123000
| Plumbing Fixtures - 2002 Addition | 1 | ea | 1 Custodial Sink need replaced/added. | 1 | 1500 | 1500 | X |  |  | 1500
HVAC
| Boiler Plant | 4000 | mbh | Modular heating water boilers installed in 1998, should be replaced with new condensing heating water boilers. | 1 | 100000 | 100000 | X |  |  | 100000
| Heating Water Supply and Return System - 1963 | 51738 | sf | Black Steel and Galvanized piping, fin-tube, supplemental heat, insulation, specialties, etc. should be replaced with a new heating water system. | 1 | 5.6 | 289732.8 | X |  |  | 289732.8
| Heating Water Supply/Return System - 1988, 1999, 2002 | 22491 | sf | Consideration could be given to adding heating water systems to serve these areas of the building. | 5 | 8.5 | 191173.5 |  | X |  |  | 191173.5
| Classroom Unit Ventilators/VRF/Mini-Splits - 1963 | 51750 | cfm | The exisitng heating only classroom unit ventilators have exceeded their useful life and should be replaced with either new heating/cooling unit ventilators or new ducted HVAC system incorporating energy recovery to pre-treat outdoor air. Consideration could be given to reuse the existing VRF/Mini-Splits and provide new 100% OA system to provide required outdoor air ventilation. | 1 | 20 | 1035000 | X |  |  | 1035000
| Rooftop Units - 1988 | 7000 | cfm | The exisitng rooftop units serving the 1988 addition have exceeded their useful life and should be replaced. | 1 | 20 | 140000 | X |  |  | 140000
| Rooftop Units - 2002 | 15250 | cfm | The VAV rooftop unit and VAV terminals were installed in 2002 and are in good condition. Consideration should be given to replacing these units in the next 5-10 years due to age. | 3 | 0 | 0 |  | X |  |  | 0
| Administration Unit | 3000 | cfm | The administration rooftop unit was installed in 2002 and is in good condition. Consideration should be given to replacing this unit in the next 5-10 years due to age. | 3 | 0 | 0 |  | X |  |  | 0
| Gymnasium Unit | 14000 | cfm | The exisitng heating and ventilating gymnasium air handling unit has exceeded its life and should be replaced with a new heating and cooling air handling unit. | 1 | 20 | 280000 | X |  |  | 280000
| Music Area Units | 3000 | cfm | The exisitng heating and ventilating music air handling units have exceeded their life and should be replaced with new heating and cooling air handling units. | 1 | 20 | 60000 | X |  |  | 60000
| Window/Portable Air-Conditioning Units | 2 | ea | The existing window air conditioning units are in fair condition, but are not very efficient. They should be removed and replaced with chilled water systems or VRF/Mini-Splits. | 5 | 0 | 0 |  | X |  | 0
| Exhaust Systems - 1963, 1988, 1999 | 59096 | sf | The toilet room and general exhaust fans are original and should be replaced. | 1 | 0.25 | 7387 | X |  |  | 7387
| Exhaust Systems - 2002 Addition | 15133 | sf | The toilet room and general exhaust fans were installed in 2002 and are in good condition. | 3 | 0 | 0 |  | X |  |  | 0
| Temperature Controls | 74229 | sf | Existing temperature controls consist a combination of pneumatic and DDC. The system needs to be replaced completely. | 1 | 4 | 296916 | X |  |  | 296916
| Chilled Water System | 250 | tons | Consideration could be given to replacing the VRF/Mini-Split cooling systems with a new chilled water system including (2) outdoor, air-cooled chillers, pumps, piping, specialties, etc. depending on what HVAC selection is made. | 5 | 1500 | 375000 |  | X |  | 375000
[6 empty] | Subtotal Project Costs | 3655297.3 |  |  | 321916 | 3142207.8 | 191173.5
[5 empty] | Design Contingency | 10% | 365529.73 |  |  | 32191.6 | 314220.78 | 19117.35
[5 empty] | Contractor General Conditions | 5% | 182764.865 |  |  | 16095.8 | 157110.39 | 9558.675
[5 empty] | Project Contingency | 7% | 255870.811 |  |  | 22534.12 | 219954.546 | 13382.145
[5 empty] | Phasing Costs | 3% | 109658.919 |  |  | 9657.48 | 94266.234 | 5735.205
[6 empty] | Estimate of Probable Construction Costs | 4459462.706 |  |  | 402395 | 3927759.75 | 238966.875
[5 empty] | Project Soft Costs | 18% | 802703.2871 |  |  | 72431.1 | 706996.755 | 43014.0375
[6 empty] | TOTAL Project Estimate of Probable Costs | 5262165.9931 |  |  | 474826.1 | 4634756.505 | 281980.9125

## Elec
Requirement Forecast Report - Electrical
Ratings to be based on the following scoring system
Client: |  | Yellow Springs School |  |  |  | 1. End of useful life |  |  |  | Prioritization Category
Campus: |  | Yellow Springs HS/MMS |  |  |  | 2. In need of Repair/Replacement |  |  |  | 1. Critial - Life Safety, Code, Technology, Security
Asset: |  | Yellow Springs HS/MMS |  |  |  | 3. Condition is satisfactory |  |  |  | 2. Priority - Infrastructure, Maintenance, Roof, Envelope
Building Area: |  | 74229 | sf |  |  | 4. Recently replaced |  |  |  | 3. Deferred - Finishes, Furnishings, Fixtures
[6 empty] | 5. New work Recommended |  | Prioritization
|  | Quantity |  | Detail (models, sizing, etc.) | Condition | Unit Cost | Total Cost | Yes | No | Critical | Priority | Deferred
Electrical
| New Generator (if sprinker piping is added) | 1 | ea | Generator, transfer switches, panels, & wiring |  | 50000 | 50000 |  | x |  |  | 50000
| Switchboards | 1 | ea | Newer existing to remain distribution panels (serving as switchgear). 1600A. | 3 | 0 | 0 |  | x |  | 0
|  | 1 | ea | Older 800A switchgear. Needs replaced. | 2 | 12000 | 12000 | x |  |  | 12000
|  | 2 | ea | Older 800A distribution panel. Needs replaced. | 2 | 12000 | 24000 | x |  |  | 24000
| Panelboards | 16 | ea | Old/Damaged Panelboards. Need Replaced. Assume 42 ckt. 225A. | 1 | 5325 | 85200 |  | x |  | 85200
|  |  | ea | Newer Undamaged Panelboards. Average of >15 year life remaining. | 3 | 0 | 0 |  | x |  |  | 0
| Interior Lighting | 74229 | sf | Circuiting as needed for new lighting fixtures denoted below | 2 | 2 | 148458 |  | x |  |  | 148458
| Classrooms | 180 | ea | T8 troffers. Upgrade to LED (number assumes 12 fixtures per classroom) | 2 | 310 | 55800 |  | x |  |  | 55800
| Labs | 96 | ea | T8 troffers. Upgrade to LED (number assumes 16 fixtures per Lab) | 2 | 310 | 29760 |  | x |  |  | 29760
| Corridors | 91 | ea | T8 troffers (primarily). Upgrade to LED | 2 | 310 | 28210 |  | x |  |  | 28210
|  | 62 | ea | 4' Direct T8 suspended fixtures. Replace with LED. | 2 | 400 | 24800 |  | x |  |  | 24800
| Gymnasium | 32 | ea | Metal halide high bay fixtures. Upgrade to LED. | 2 | 775 | 24800 |  | x |  |  | 24800
| Cafeteria | 48 | ea | 4' Direct/Indirect T8 suspended fixtures. Replace with LED. | 2 | 400 | 19200 |  | x |  |  | 19200
| Kitchen | 78 | ea | Shop Lights. Upgrade to LED. | 2 | 310 | 24180 |  | x |  |  | 24180
| Media Center | 35 | ea | T8 Troffers. Upgrade all to LED. | 2 | 310 | 10850 |  | x |  |  | 10850
| Administration | 6 | ea | T8 troffers. Upgrade to LED. | 2 | 310 | 1860 |  | x |  |  | 1860
|  | 70 | ea | 4' Direct T8 suspended fixtures. Replace with LED. | 2 | 400 | 28000 |  | x |  |  | 28000
| Restroom | 22 | ea | T8 troffers (18). T8 suspended direct/indirect lights (4). Upgrade to LED. | 2 | 350 | 7700 |  | x |  |  | 7700
| Lighting Controls | 74229 | sf | Low voltage wiring, occupancy sensors, etc. |  | 2 | 148458 |  | x |  |  | 148458
| Switching (2 per classroom & lab, all else 1) | 64 | ea | Good Condition. | 3 | 0 | 0 |  | x |  |  | 0
|  | 64 | ea | Damaged/Aged. (50%) | 2 | 120 | 7680 |  | x |  | 7680
| Classroom Receptacles | 60 | ea | Good Condition. | 3 | 0 | 0 |  | x |  |  | 0
|  | 60 | ea | Damaged/Aged. (50%) | 2 | 250 | 15000 |  | x |  | 15000
| Lab Receptacles | 48 | ea | Good Condition. | 3 | 0 | 0 |  | x |  |  | 0
|  | 48 | ea | Damaged/Aged. (50%) | 2 | 250 | 12000 |  | x |  | 12000
| Corridor Receptacles | 30 | ea | Good Condition. | 3 | 0 | 0 |  | x |  |  | 0
|  | 30 | ea | Damaged/Aged. (50%) | 2 | 250 | 7500 |  | x |  | 7500
| Receptacles - All other areas (average of 4 per area) | 154 | ea | Good Condition. | 3 | 0 | 0 |  | x |  |  | 0
|  | 154 | ea | Damaged/Aged. (50%) | 2 | 250 | 38500 |  | x |  | 38500
| Receptacle Circuiting | 74229 | sf | Replacements circuits as needed for receptacles | 2 | 1.5 | 111343.5 |  | x |  | 111343.5
| Mechanical Equipment Power | 74229 | sf | Disconnect and reconnect HVAC systems | 2 | 1.5 | 111343.5 |  | x |  | 111343.5
| Fire Alarm System | 74229 | sf | Provide new voice evacuation style as currently required by code. | 2 | 2 | 148458 | x |  | 148458
| Exit/Emergency Lighting | 74229 | sf | All exit signs and emergency lights should be replaced. | 2 | 1 | 74229 | x |  | 74229
[6 empty] | Project Subtotal | 1249330 |  |  | 222687 | 424567 | 602076
[5 empty] | Design Contingency | 10% | 124933 |  |  | 22268.7 | 42456.7 | 60207.6
[5 empty] | Contractor General Conditions | 5% | 62466.5 |  |  | 11134.35 | 21228.35 | 30103.8
[5 empty] | Project Contingency | 7% | 87453.1 |  |  | 15588.09 | 29719.69 | 42145.32
[5 empty] | Phasing Costs | 3% | 37479.9 |  |  | 6680.61 | 12737.01 | 18062.28
[6 empty] | Estimate of Probable Construction Costs | 1561662.5 |  |  | 278358.75 | 530708.75 | 752595
[6 empty] | 18% | 281099.25 |  |  | 50104.575 | 95527.575 | 135467.1
[6 empty] | TOTAL Project Estimate of Probable Costs | 1842761.75 |  |  | 328463.325 | 626236.325 | 888062.1

## Tech
Requirement Forecast Report - Technology
Ratings to be based on the following scoring system
Client: |  | Yellow Springs School |  |  |  | 1. End of useful life |  |  |  | Prioritization Category
Campus: |  | Yellow Springs HS/MMS |  |  |  | 2. In need of Repair/Replacement |  |  |  | 1. Critial - Life Safety, Code, Technology, Security
Asset: |  | Yellow Springs HS/MMS |  |  |  | 3. Condition is satisfactory |  |  |  | 2. Priority - Infrastructure, Maintenance, Roof, Envelope
Building Area: |  | 74229 | sf |  |  | 4. Recently replaced |  |  |  | 3. Deferred - Finishes, Furnishings, Fixtures
[6 empty] | 5. New work Recommended |  | Prioritization
Technology |  | Quantity |  | Detail (models, sizing, etc.) | Condition | Unit Cost | Total Cost | Yes | No | Critical | Priority | Deferred
Technology
| Paging System and Speakers | 74229 | sf | The existing Dukane paging system has reached the end of it's life. Replacement parts and support are not available for the existing system since the manufacturer is no longer in business. It is recommended that a new paging system be provided for the entire building. This would include a new headend, new speakers, and new cabling. | 1 | 0.75 | 55671.75 | X |  | 55671.75
| Clock System | 74229 | sf | There is currently no synchronous clock system. It is recommended the entire building be provided with a synchronous clock system that is tied into other systems within the building. | 1 | 0.4 | 29691.6 |  | X |  |  | 29691.6
| Phone System and Phones | 60 | ea | The existing phone system functions but consistently drops out multiple times a month. It is recommended that a new IP phone system be provided. This will include a new phone switch or managed system, and all new IP phones. | 2 | 675 | 40500 | X |  | 40500
| Horizontal Cabling Infrastructure | 74229 | sf | The data cabling in the building is currently a mixture of Category 5E and 6. It is recommended that the cabling to support wireless access points be upgraded to shielded Category 6A to support higher bandwidth. This will allow the wireless network to support more wireless devices at higher speeds. It is also recommended that all the Category 5e cabling in the building be replaced with Category 6 cabling. This will also support higher bandwidth. | 3 | 1.8 | 133612.2 |  | X |  | 133612.2
| Fiber Backbone Cabling Infrastructure | 1100 | lf | The existing fiber backbone is currently 62.5 multi-mode fiber optic cable. This will only support a 1 Gb backbone for the network. It is recommended that this cable be replaced with 50 micron multi-mode fiber optic cable. This will support a 10 Gb backbone to support higher bandwidth speeds and more devices on the network. | 1 | 8 | 8800 | X |  | 8800
| Pathways for Horizontal Data Cabling | 74229 | sf | A majority of the data cabling and video input cabling is exposed and not properly supported. There are many locations where the cabling is coming straight down from the ceiling to the device it's connected to. It is recommended that all new pathways be provided to support the horizontal data cabling and video input cabling. | 2 | 1 | 74229 |  | X |  | 74229
| Classroom AV Cabling | 25 | ea | The existing AV cabling is classrooms is analog VGA cabling. When computers are refreshed, the newer computers will no longer support analog VGA video. It is recommended that the classrooms be upgraded with digital HDMI cabling between the teacher's computer and video display. | 2 | 495 | 12375 | X |  |  | 12375
| Classroom Displays | 15 | ea | There is a mixture of new Ultra Short-throw projectors and older discontinued LCD projectors in the building. It is recommended that the older LCD projectors be replaced with the new ultra-short throw projectors. | 2 | 2750 | 41250 | X |  |  | 41250
| Classroom Sound Systems | 25 | ea | There are currently no Classroom Sound Systems. It is recommended that at a minimum a new small amplifier and 2 ceiling speakers be provided in each room for the audio from the teacher's PC to be evenly distributed in the room. | 1 | 1200 | 30000 |  | X |  |  | 30000
| Network Switching | 74229 | sf | It is recommended that the network switches be replaced to support a 10 Gb network. There are also currently no UPS's installed in the building and there have been power issues. It is recommended that new UPS's be provided in each technology cabinet/rack. | 2 | 1.1 | 81651.9 | X |  | 81651.9
| Wireless Network | 74229 | sf | The existing wireless network was installed in the summer of 2018. The existing wireless network does not need to be replaced | 4 | 1.25 | 0 |  | X |  |  | 0
Security
| Access Control | 7 | ea | Currently there is no Access Control System in the school. An access control system is recommended to be provided with card readers at 7 doors. | 1 | 6000 | 42000 | X |  | 42000
| Video Surviellance | 0 | ea | The security camera system was recently upgraded 2 years ago. There is adequate coverage at the school. | 4 | 1300 | 0 |  | X |  |  | 0
| Intrusion Detection | 74229 | sf | There is currently some intrusion detection installed in the school. A new intrusion detection system is recommended for the entire first floor. This would be accomplished by providing door contacts on all exterior doors and motion detectors on the first floor. | 2 | 0.69 | 51218.01 | X |  | 51218.01
[6 empty] | Subtotal Project Costs | 600999.46 |  |  | 279841.66 | 261466.2 | 59691.6
[5 empty] | Design Contingency | 10% | 60099.946 |  |  | 27984.166 | 26146.62 | 5969.16
[5 empty] | Contractor General Conditions | 5% | 30049.973 |  |  | 13992.083 | 13073.31 | 2984.58
[5 empty] | Project Contingency | 7% | 42069.9622 |  |  | 19588.9162 | 18302.634 | 4178.412
[5 empty] | Phasing Costs | 3% | 18029.9838 |  |  | 8395.2498 | 7843.986 | 1790.748
[6 empty] | TOTAL Estimate of Probable Costs | 751249.325 |  |  | 349802.075 | 326832.75 | 74614.5
[5 empty] | Project Soft Costs | 18% | 135224.8785 |  |  | 62964.3735 | 58829.895 | 13430.61
[6 empty] | TOTAL Project Estimate of Probable Costs | 886474.2035 |  |  | 412766.4485 | 385662.645 | 88045.11

## Site
Requirement Forecast Report - Site
Ratings to be based on the following scoring system
Client: |  | Yellow Springs School |  |  |  | 1. End of useful life |  |  |  | Prioritization Category
Campus: |  | Yellow Springs HS/MMS |  |  |  | 2. In need of Repair/Replacement |  |  |  | 1. Critial - Life Safety, Code, Technology, Security
Asset: |  | Yellow Springs HS/MMS |  |  |  | 3. Condition is satisfactory |  |  |  | 2. Priority - Infrastructure, Maintenance, Roof, Envelope
Site Area: |  | 34.97 | acre |  |  | 4. Recently replaced |  |  |  | 3. Deferred - Finishes, Furnishings, Fixtures
[6 empty] | 5. New work Recommended |  | Prioritization
Drives and Parking |  | Quantity |  | Detail (models, sizing, etc.) | Condition | Unit Cost | Total Cost | Yes | No | Critical | Priority | Deferred
| Provide off-street ADA Parking | 6 | ea | Construct parking on site with access to the main entry for three ADA parking spaces and three spaces with access to either the main entrance or an alterantive accessible entrance. | 5 | 4000 | 24000 | X |  | 24000
| Provide improve student drop-off lane | 2000 | sf | Provide designated student drop off lane that is clearly marked with and unobstructed walkway to the main entrance. | 5 | 7.2222 | 14444.4444 | X |  | 14444.4444
| Crack and seal coat student parking lot | 63623 | sf | Crack Seal, seal coat and pavement markings | 3 | 0.5 | 31811.5 |  | X |  |  | 31811.5
| Reconstruct main entry parking, staff parking and access drive. | 30260 | sf | Full resconstruction with standard duty asphalt pavement. | 2 | 7.22 | 218477.2 | X |  |  | 218477.2
| Extend the concrete dumpster pad | 300 | sf | 6" steel reinforced concrete thicked at the edges | 2 | 8 | 2400 | X |  |  | 2400
Walks and Access
| Remove and replace front walks and walks directly adjacent to the building. | 5300 | sf | Remove exisiting walk and prepare base for new 8' wide 4" thick concrete walk. | 1 | 6 | 31800 | X |  |  | 31800
| Install vertical curb to provide separation between vehicles and pedestrians where possible. This will require draiange improvments, see drainage section. | 400 | lf | Install integral vertical curb as part of sidewalk replacement at main entry and student drop off areas. | 5 | 20 | 8000 | X |  | 8000
| Install concrete walk for egress from all exit doors. | 1765 | sf | Prepare base and install new 6' wide 4" thick concrete walk. | 5 | 6 | 10590 | X |  | 10590
| Remove and replace concrete in the courtyard as part of the reconstruction of the 1988 addition. | 5084 | sf | Concrete walks, ramps and steel handrails with plantings. | 1 | 12 | 61008 | X |  | 61008
Site Safety and Security
| Replace steel hand rail at basment stiars | 35 | lf | Painted steel guardrail | 2 | 60 | 2100 | X |  | 2100
| Fence at stadium has been damaged and needs to be repaired or replaced. | 370 | lf | 10' tall chain link fence with midrail | 2 | 85 | 31450 | X |  |  | 31450
Site Drainage
| Provide subsurface draiange with stormwater inlets as part of drive and walkway seperation work | 1 | ls | To provide veritcal seperation between pedestrians and vehicles at the front entry and student drop off areas, the access drive must be lowered and a storm drianage system installed. | 5 | 45000 | 45000 | X |  | 45000
Base Site Work Allowance
| Site Work Allowance | 74229 | sf | Provide $1.50 per building square footage. | 2 | 1.5 | 111343.5 | X |  | 111343.5
[6 empty] | Subtotal Project Cost | 592424.6444 |  |  | 276485.9444 | 284127.2 | 31811.5
[5 empty] | Estimate Contingency | 10% | 59242.4644 |  |  | 27648.5944 | 28412.72 | 3181.15
[5 empty] | Contractor General Conditions | 5% | 29621.2322 |  |  | 13824.2972 | 14206.36 | 1590.575
[5 empty] | Project Contingency | 7% | 41469.7251 |  |  | 19354.0161 | 19888.904 | 2226.805
[5 empty] | Phasing Costs | 3% | 17772.7393 |  |  | 8294.5783 | 8523.816 | 954.345
[6 empty] | Estimate of Probable Construction Costs | 740530.8056 |  |  | 345607.4306 | 355159 | 39764.375
[5 empty] | Project Soft Costs | 18% | 133295.545 |  |  | 62209.3375 | 63928.62 | 7157.5875
[6 empty] | TOTAL Project Estimate of Probable Costs | 873826.3506 |  |  | 407816.7681 | 419087.62 | 46921.9625